## English
PUMP SIZING CALCULATION
CheGuide.com | [8 empty] | Tag No. |  | P-101 |  |  |  |  | Suction Calculations |  |  |  | Outlet Calculations |  |  |  |  | Head Equation (2nd Order Curve Fitting)
Chemical Engineer's Guide | [8 empty] | Description |  | Feed Pump | [13 empty] | -0.0019957 | -0.10066 | 149.9348
[9 empty] | Date |  | 06-May-2017 |  |  |  |  | Selected ID |  | 6 |  | Selected ID |  | 6 |  |  | 8.9021e-06 | 0.0019848 | 0.083448
User Input | [8 empty] | By |  | CheGuide |  |  |  |  | Selected Schedule |  | 7 |  | Selected Schedule |  | 7 |  |  | 1 | 0.10519 | #N/A
[16 empty] | Pipe ID Selected |  | 3.068 | inch | Pipe ID Selected |  | 3.068 | inch
[18 empty] | 3.068 | inch |  |  | 3.068 | inch |  | Efficiency Equation (2nd Order Curve Fitting)
[16 empty] | Area |  | 0.051338 | ft2 | Area |  | 0.051338 | ft2 |  | -0.0017458 | 0.42345 | 20.1368
Flowrate |  |  | 100 | US gpm | [11 empty] | Velocity |  | 4.3399 | ft/s | Velocity |  | 4.3399 | ft/s |  | 1.5633e-05 | 0.0034856 | 0.14655
Density |  |  | 62.4 | lb/ft3 | [11 empty] | Re |  | 103035.8491 |  | Re |  | 103035.8491 |  |  | 0.99955 | 0.18473 | #N/A
Viscosity |  |  | 1 | cP | [11 empty] | e/D |  | 0.0005867 |  | e/D |  | 0.0005867
Vapor Pressure |  |  | 15 | psia | [11 empty] | A |  | 4.9554e+20 |  | A |  | 4.9554e+20 |  |  | System Curve (2nd Order Curve Fitting)
[16 empty] | B |  | 9.5994e-08 |  | B |  | 9.5994e-08 |  |  | 0.0011033 | 0.013867 | 100.7739
Differential DP |  |  | 49.0084 | psi | [11 empty] | f |  | 0.020711 |  | f |  | 0.020711 |  |  | 2.3589e-06 | 0.0004398 | 0.017082
Differential Head |  |  | 113.2094 | ft | [11 empty] | DP1 |  | 1.0267 | psi/100ft | DP |  | 1.0267 | psi/100ft |  | 1 | 0.028618 | #N/A
Hydraulic power |  |  | 2.8588 | bhp | [11 empty] | Pressure |  | 20.5718 | psi | Pressure |  | 69.5802
NPSH available |  |  | 12.8709 | ft | [20 empty] | Solution of System & Head Curve | [5 empty] | Efficiency | 45.5429 | %
[25 empty] | -0.003099 | -0.11453 | 49.1609
Suction Condition | [7 empty] | Discharge Condition | [7 empty] | Curve Fitting |  |  |  |  | Maximum Flow |  | 180
Pressure |  | P1 | 25 | psia |  |  |  | Pressure |  | P2 | 50 | psia | [8 empty] | Division |  | 20 |  | Determinant |  | 0.62251 | TRUE | 0.78899 |  |  | X | Y
Static Head |  | h1 | 5 | ft |  |  |  | Static Head |  | h2 | 25 | ft |  |  |  | Flow | Head | Efficiency |  |  | Increment |  | 9 |  | Roots |  | -145.777 | 108.8206 |  |  |  | 108.8206 | 0
Equipment DP |  |  | 5 | psi |  |  |  | Equipment DP |  |  | 5 | psi |  |  | 1 | 0 | 150 | 20 | [6 empty] | Selected Flow |  | 108.8206 | GPM | Head | 115.3477 | ft | 108.8206 | 115.3477
Misc DP |  |  | 0 | psi |  |  |  | Misc DP |  |  | 0 | psi |  |  | 2 | 20 | 147 | 28 |  |  |  | Suction Pipe
[15 empty] | 3 | 50 | 140 | 37 |  |  | Flow | Velocity | Reynold | A | B | f | DP1 | Elb, 90LR | Elb, 45LR | Tees, Thru | Tees, Bran | Ball | Butterfly | Gate | Globe | Check | Plug | Pipe | Sum K | DP | Suct P | Diff P | System Curve | Pump Head | Efficiency %
Piping | [7 empty] | Piping | [6 empty] | 4 | 80 | 129 | 43 |  |  | GPM | ft/s | [5 empty] | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | [6 empty] | %
Length |  | L1 | 120 | ft |  |  |  | Length |  | L2 | 300 | ft |  |  | 5 | 100 | 120 | 45 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.1645 | 43.658 | 100.85 | 149.9348 | 20.1368
Pipe Diameter |  |  | 3 | inch |  |  |  | Pipe Diameter |  |  | 3 | inch |  |  | 6 | 150 | 90 | 44 |  | 2 | 9 | 0.39059 | 9273.2264 | 1.3052e+19 | 5180398960.7026 | 0.032631 | 0.013102 | 0.35146 | 0.25281 | 0.67915 | 1.147 | 0.25281 | 0.41776 | 0.16495 | 5.4655 | 2.1507 | 0.43932 | 0.51725 | 3.1126 | 0.0031947 | 22.1456 | 43.7221 | 100.9981 | 148.8672 | 23.8064
Sch/ Thick |  |  | 40 |  |  |  |  | Sch/ Thick |  |  | 40 |  |  |  | 7 | 180 | 67 | 40 |  | 3 | 18 | 0.78118 | 18546.4528 | 4.8691e+19 | 79046.615 | 0.02768 | 0.044455 | 0.30832 | 0.22585 | 0.67106 | 1.1039 | 0.22585 | 0.37462 | 0.14877 | 5.3847 | 2.0698 | 0.3854 | 0.50863 | 2.9665 | 0.012179 | 22.099 | 43.8796 | 101.3619 | 147.4763 | 27.1932
Pipe ID |  | ID1 | 3.068 | inch |  |  |  | Pipe ID |  | ID2 | 3.068 | inch |  |  | 8 | 200 | 50 | 35 |  | 4 | 27 | 1.1718 | 27819.6793 | 9.5328e+19 | 120.3436 | 0.02545 | 0.091968 | 0.29395 | 0.21686 | 0.66836 | 1.0895 | 0.21686 | 0.36024 | 0.14338 | 5.3577 | 2.0428 | 0.36743 | 0.50575 | 2.9178 | 0.026952 | 22.0272 | 44.1216 | 101.9209 | 145.7621 | 30.2972
[15 empty] | 9 | 200 | 50 | 35 |  | 5 | 36 | 1.5624 | 37092.9057 | 1.4673e+20 | 1.2062 | 0.024114 | 0.15492 | 0.28676 | 0.21237 | 0.66702 | 1.0823 | 0.21237 | 0.35305 | 0.14068 | 5.3442 | 2.0294 | 0.35845 | 0.50431 | 2.8935 | 0.047515 | 21.9311 | 44.4452 | 102.6683 | 143.7246 | 33.1183
Roughness |  |  | 0.0018 | inch |  |  |  | Roughness |  |  | 0.0018 | inch |  |  | 10 | 200 | 50 | 35 |  | 6 | 45 | 1.953 | 46366.1321 | 1.9965e+20 | 0.03395 | 0.023204 | 0.23292 | 0.28244 | 0.20968 | 0.66621 | 1.078 | 0.20968 | 0.34874 | 0.13906 | 5.3361 | 2.0213 | 0.35305 | 0.50345 | 2.8789 | 0.073868 | 21.8111 | 44.8486 | 103.6003 | 141.3637 | 35.6567
[20 empty] | 7 | 54 | 2.3435 | 55639.3585 | 2.5233e+20 | 0.0018363 | 0.022534 | 0.32573 | 0.27957 | 0.20788 | 0.66567 | 1.0751 | 0.20788 | 0.34586 | 0.13799 | 5.3307 | 2.0159 | 0.34946 | 0.50288 | 2.8691 | 0.10601 | 21.6676 | 45.3309 | 104.7144 | 138.6796 | 37.9122
Fittings |  |  | No. | K | DP |  |  | Fittings |  |  | No. | K | DP | [6 empty] | 8 | 63 | 2.7341 | 64912.5849 | 3.0381e+20 | 0.00015588 | 0.022017 | 0.43318 | 0.27751 | 0.20659 | 0.66528 | 1.0731 | 0.20659 | 0.34381 | 0.13722 | 5.3269 | 2.012 | 0.34689 | 0.50246 | 2.8622 | 0.14394 | 21.5007 | 45.8914 | 106.0092 | 135.6722 | 39.8849
Elbows, 90LR |  |  | 1 | 0.27295 | 0.034586 |  |  | Elbows, 90LR |  |  | 1 | 0.27295 | 0.034586 | [6 empty] | 9 | 72 | 3.1247 | 74185.8114 | 3.5359e+20 | 1.8404e-05 | 0.021604 | 0.55515 | 0.27597 | 0.20563 | 0.66499 | 1.0715 | 0.20563 | 0.34227 | 0.13664 | 5.324 | 2.0091 | 0.34497 | 0.50216 | 2.8569 | 0.18766 | 21.3107 | 46.5296 | 107.4835 | 132.3414 | 41.5748
Elbows, 45LR |  |  | 1 | 0.20374 | 0.025816 |  |  | Elbows, 45LR |  |  | 1 | 0.20374 | 0.025816 | [6 empty] | 10 | 81 | 3.5153 | 83459.0378 | 4.0141e+20 | 2.7957e-06 | 0.021264 | 0.69156 | 0.27477 | 0.20488 | 0.66477 | 1.0703 | 0.20488 | 0.34107 | 0.13619 | 5.3218 | 2.0069 | 0.34347 | 0.50192 | 2.8529 | 0.23717 | 21.0975 | 47.2452 | 109.1363 | 128.6874 | 42.9818
Tees, Thru |  |  | 1 | 0.66443 | 0.08419 |  |  | Tees, Thru |  |  | 1 | 0.66443 | 0.08419 | [6 empty] | 11 | 90 | 3.9059 | 92732.2642 | 4.4715e+20 | 5.1804e-07 | 0.020979 | 0.84234 | 0.27382 | 0.20428 | 0.66459 | 1.0694 | 0.20428 | 0.34011 | 0.13583 | 5.32 | 2.0051 | 0.34227 | 0.50173 | 2.8496 | 0.29247 | 20.8612 | 48.0377 | 110.9671 | 124.71 | 44.1061
Tees, Branch |  |  | 1 | 1.0685 | 0.13539 |  |  | Tees, Branch |  |  | 1 | 1.0685 | 0.13539 | [6 empty] | 12 | 99 | 4.2965 | 102005.4906 | 4.9082e+20 | 1.1274e-07 | 0.020736 | 1.0074 | 0.27303 | 0.20379 | 0.66444 | 1.0686 | 0.20379 | 0.33933 | 0.13554 | 5.3185 | 2.0036 | 0.34129 | 0.50157 | 2.847 | 0.35356 | 20.602 | 48.9071 | 112.9753 | 120.4094 | 44.9475
Ball Valves |  |  |  | 0.20374 |  |  |  | Ball Valves |  |  |  | 0.20374 | [7 empty] | 13 | 108 | 4.6871 | 111278.7171 | 5.3245e+20 | 2.802e-08 | 0.020526 | 1.1868 | 0.27238 | 0.20339 | 0.66432 | 1.0679 | 0.20339 | 0.33868 | 0.13529 | 5.3173 | 2.0024 | 0.34047 | 0.50144 | 2.8448 | 0.42044 | 20.3199 | 49.853 | 115.1605 | 115.7854 | 45.506
Butterfly Valves |  |  |  | 0.33925 |  |  |  | Butterfly Valves |  |  |  | 0.33925 | [7 empty] | 14 | 117 | 5.0777 | 120551.9435 | 5.7211e+20 | 7.7852e-09 | 0.020343 | 1.3804 | 0.27183 | 0.20304 | 0.66422 | 1.0674 | 0.20304 | 0.33812 | 0.13508 | 5.3162 | 2.0014 | 0.33978 | 0.50133 | 2.8429 | 0.49311 | 20.0149 | 50.8754 | 117.5223 | 110.8381 | 45.7818
Gate Valves |  |  | 1 | 0.13551 | 0.01717 |  |  | Gate Valves |  |  | 1 | 0.13551 | 0.01717 | [6 empty] | 15 | 126 | 5.4683 | 129825.1699 | 6.0989e+20 | 2.3786e-09 | 0.020181 | 1.5882 | 0.27135 | 0.20274 | 0.66413 | 1.0669 | 0.20274 | 0.33765 | 0.13491 | 5.3153 | 2.0005 | 0.33919 | 0.50123 | 2.8413 | 0.57157 | 19.6871 | 51.9742 | 120.0603 | 105.5675 | 45.7748
Globe Valves |  |  |  | 5.3183 |  |  |  | Globe Valves |  |  |  | 5.3183 | [7 empty] | 16 | 135 | 5.8589 | 139098.3963 | 6.4588e+20 | 7.8868e-10 | 0.020036 | 1.8101 | 0.27094 | 0.20249 | 0.66405 | 1.0665 | 0.20249 | 0.33724 | 0.13475 | 5.3146 | 1.9997 | 0.33868 | 0.50115 | 2.8399 | 0.65581 | 19.3365 | 53.1491 | 122.7745 | 99.9737 | 45.4849
Check Valves |  |  |  | 2.0035 |  |  |  | Check Valves |  |  | 1 | 2.0035 | 0.25386 | [6 empty] | 17 | 144 | 6.2494 | 148371.6227 | 6.8019e+20 | 2.8083e-10 | 0.019907 | 2.0462 | 0.27058 | 0.20226 | 0.66398 | 1.0661 | 0.20226 | 0.33688 | 0.13462 | 5.3139 | 1.999 | 0.33823 | 0.50108 | 2.8387 | 0.74585 | 18.9632 | 54.4002 | 125.6645 | 94.0565 | 44.9122
Plug Valves |  |  |  | 0.34119 |  |  |  | Plug Valves |  |  |  | 0.34119 | [7 empty] | 18 | 153 | 6.64 | 157644.8492 | 7.1291e+20 | 1.0646e-10 | 0.019791 | 2.2965 | 0.27026 | 0.20206 | 0.66392 | 1.0658 | 0.20206 | 0.33656 | 0.1345 | 5.3133 | 1.9984 | 0.33783 | 0.50101 | 2.8376 | 0.84167 | 18.567 | 55.7274 | 128.7302 | 87.816 | 44.0566
Pipe Entrance |  |  | 1 | 0.50155 | 0.063552 |  |  | Pipe Exit |  |  | 1 | 1 | 0.12671 | [6 empty] | 19 | 162 | 7.0306 | 166918.0756 | 7.4413e+20 | 4.2658e-11 | 0.019685 | 2.5608 | 0.26998 | 0.20189 | 0.66387 | 1.0655 | 0.20189 | 0.33628 | 0.13439 | 5.3128 | 1.9979 | 0.33748 | 0.50096 | 2.8366 | 0.94329 | 18.1482 | 57.1305 | 131.9714 | 81.2522 | 42.9183
[5 empty] | 0.36071 | [7 empty] | 0.67772 | [6 empty] | 20 | 171 | 7.4212 | 176191.302 | 7.7394e+20 | 1.796e-11 | 0.019589 | 2.8393 | 0.26973 | 0.20173 | 0.66382 | 1.0653 | 0.20173 | 0.33603 | 0.1343 | 5.3123 | 1.9974 | 0.33716 | 0.50091 | 2.8358 | 1.0507 | 17.7066 | 58.6095 | 135.388 | 74.365 | 41.4971
Velocity |  |  | 4.3399 | ft/s |  |  |  | Velocity |  |  | 4.3399 | ft/s | [7 empty] | 21 | 180 | 7.8118 | 185464.5284 | 8.0243e+20 | 7.9047e-12 | 0.0195 | 3.1319 | 0.2695 | 0.20159 | 0.66378 | 1.0651 | 0.20159 | 0.3358 | 0.13421 | 5.3119 | 1.997 | 0.33688 | 0.50086 | 2.835 | 1.1639 | 17.2424 | 60.1644 | 138.9798 | 67.1546 | 39.7931
Reynold's No. |  |  | 103035.8491 |  |  |  |  | Reynold's No. |  |  | 103035.8491
Pipe DP |  |  | 1.0267 | psi/100ft |  |  |  | Pipe DP |  |  | 1.0267 | psi/100ft | [9 empty] | Discharge Conditions
Suction Pressure |  |  | 20.5718 | psia |  |  |  | Discharge Pressure |  |  | 69.5802 | psia | [8 empty] | Flow | Velocity | Reynold | A | B | f | DP1 | Elb, 90LR | Elb, 45LR | Tees, Thru | Tees, Bran | Ball | Butterfly | Gate | Globe | Check | Plug | Pipe | Sum K | DP | Disch P
[21 empty] | GPM | ft/s | [5 empty] | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 1
[20 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 65.8225
| Pump Manufacturer's Curve | [6 empty] | Maximum Flow |  |  | 180 | US gpm | [7 empty] | 2 | 9 | 0.39059 | 9273.2264 | 1.3052e+19 | 5180398960.7026 | 0.032631 | 0.013102 | 0.35146 | 0.25281 | 0.67915 | 1.147 | 0.25281 | 0.41776 | 0.16495 | 5.4655 | 2.1507 | 0.43932 | 1 | 5.7461 | 0.0058975 | 65.8677
[8 empty] | Flow value till which System and Head Curve | [11 empty] | 3 | 18 | 0.78118 | 18546.4528 | 4.8691e+19 | 79046.615 | 0.02768 | 0.044455 | 0.30832 | 0.22585 | 0.67106 | 1.1039 | 0.22585 | 0.37462 | 0.14877 | 5.3847 | 2.0698 | 0.3854 | 1 | 5.5277 | 0.022693 | 65.9786
| Flow | Head | Efficiency |  |  |  |  | are calculated | [11 empty] | 4 | 27 | 1.1718 | 27819.6793 | 9.5328e+19 | 120.3436 | 0.02545 | 0.091968 | 0.29395 | 0.21686 | 0.66836 | 1.0895 | 0.21686 | 0.36024 | 0.14338 | 5.3577 | 2.0428 | 0.36743 | 1 | 5.4549 | 0.050388 | 66.1488
| gpm | ft | % | [16 empty] | 5 | 36 | 1.5624 | 37092.9057 | 1.4673e+20 | 1.2062 | 0.024114 | 0.15492 | 0.28676 | 0.21237 | 0.66702 | 1.0823 | 0.21237 | 0.35305 | 0.14068 | 5.3442 | 2.0294 | 0.35845 | 1 | 5.4185 | 0.088981 | 66.3762
| 0 | 150 | 20 |  |  |  |  | Operating Conditions | [11 empty] | 6 | 45 | 1.953 | 46366.1321 | 1.9965e+20 | 0.03395 | 0.023204 | 0.23292 | 0.28244 | 0.20968 | 0.66621 | 1.078 | 0.20968 | 0.34874 | 0.13906 | 5.3361 | 2.0213 | 0.35305 | 1 | 5.3967 | 0.13847 | 66.6597
| 20 | 147 | 28 |  |  |  |  | Flowrate |  |  | 108.8206 | US gpm | [7 empty] | 7 | 54 | 2.3435 | 55639.3585 | 2.5233e+20 | 0.0018363 | 0.022534 | 0.32573 | 0.27957 | 0.20788 | 0.66567 | 1.0751 | 0.20788 | 0.34586 | 0.13799 | 5.3307 | 2.0159 | 0.34946 | 1 | 5.3821 | 0.19886 | 66.9985
| 50 | 140 | 37 |  |  |  |  | Head |  |  | 115.3477 | ft | [7 empty] | 8 | 63 | 2.7341 | 64912.5849 | 3.0381e+20 | 0.00015588 | 0.022017 | 0.43318 | 0.27751 | 0.20659 | 0.66528 | 1.0731 | 0.20659 | 0.34381 | 0.13722 | 5.3269 | 2.012 | 0.34689 | 1 | 5.3717 | 0.27015 | 67.3922
| 80 | 129 | 43 |  |  |  |  | Efficiency |  |  | 45.5429 | % | [7 empty] | 9 | 72 | 3.1247 | 74185.8114 | 3.5359e+20 | 1.8404e-05 | 0.021604 | 0.55515 | 0.27597 | 0.20563 | 0.66499 | 1.0715 | 0.20563 | 0.34227 | 0.13664 | 5.324 | 2.0091 | 0.34497 | 1 | 5.3639 | 0.35234 | 67.8403
| 100 | 120 | 45 |  |  |  |  | Hydraulic Power |  |  | 3.1697 | bhp | [7 empty] | 10 | 81 | 3.5153 | 83459.0378 | 4.0141e+20 | 2.7957e-06 | 0.021264 | 0.69156 | 0.27477 | 0.20488 | 0.66477 | 1.0703 | 0.20488 | 0.34107 | 0.13619 | 5.3218 | 2.0069 | 0.34347 | 1 | 5.3578 | 0.44542 | 68.3426
| 150 | 90 | 44 |  |  |  |  | Rated Power |  |  | 6.9599 | bhp | [7 empty] | 11 | 90 | 3.9059 | 92732.2642 | 4.4715e+20 | 5.1804e-07 | 0.020979 | 0.84234 | 0.27382 | 0.20428 | 0.66459 | 1.0694 | 0.20428 | 0.34011 | 0.13583 | 5.32 | 2.0051 | 0.34227 | 1 | 5.353 | 0.54941 | 68.8989
| 180 | 67 | 40 | [16 empty] | 12 | 99 | 4.2965 | 102005.4906 | 4.9082e+20 | 1.1274e-07 | 0.020736 | 1.0074 | 0.27303 | 0.20379 | 0.66444 | 1.0686 | 0.20379 | 0.33933 | 0.13554 | 5.3185 | 2.0036 | 0.34129 | 1 | 5.349 | 0.66429 | 69.5091
| 200 | 50 | 35 | [16 empty] | 13 | 108 | 4.6871 | 111278.7171 | 5.3245e+20 | 2.802e-08 | 0.020526 | 1.1868 | 0.27238 | 0.20339 | 0.66432 | 1.0679 | 0.20339 | 0.33868 | 0.13529 | 5.3173 | 2.0024 | 0.34047 | 1 | 5.3457 | 0.79007 | 70.1729
[20 empty] | 14 | 117 | 5.0777 | 120551.9435 | 5.7211e+20 | 7.7852e-09 | 0.020343 | 1.3804 | 0.27183 | 0.20304 | 0.66422 | 1.0674 | 0.20304 | 0.33812 | 0.13508 | 5.3162 | 2.0014 | 0.33978 | 1 | 5.3429 | 0.92675 | 70.8904
[20 empty] | 15 | 126 | 5.4683 | 129825.1699 | 6.0989e+20 | 2.3786e-09 | 0.020181 | 1.5882 | 0.27135 | 0.20274 | 0.66413 | 1.0669 | 0.20274 | 0.33765 | 0.13491 | 5.3153 | 2.0005 | 0.33919 | 1 | 5.3405 | 1.0743 | 71.6613
[20 empty] | 16 | 135 | 5.8589 | 139098.3963 | 6.4588e+20 | 7.8868e-10 | 0.020036 | 1.8101 | 0.27094 | 0.20249 | 0.66405 | 1.0665 | 0.20249 | 0.33724 | 0.13475 | 5.3146 | 1.9997 | 0.33868 | 1 | 5.3384 | 1.2328 | 72.4857
[20 empty] | 17 | 144 | 6.2494 | 148371.6227 | 6.8019e+20 | 2.8083e-10 | 0.019907 | 2.0462 | 0.27058 | 0.20226 | 0.66398 | 1.0661 | 0.20226 | 0.33688 | 0.13462 | 5.3139 | 1.999 | 0.33823 | 1 | 5.3366 | 1.4022 | 73.3634
[20 empty] | 18 | 153 | 6.64 | 157644.8492 | 7.1291e+20 | 1.0646e-10 | 0.019791 | 2.2965 | 0.27026 | 0.20206 | 0.66392 | 1.0658 | 0.20206 | 0.33656 | 0.1345 | 5.3133 | 1.9984 | 0.33783 | 1 | 5.335 | 1.5824 | 74.2944
[20 empty] | 19 | 162 | 7.0306 | 166918.0756 | 7.4413e+20 | 4.2658e-11 | 0.019685 | 2.5608 | 0.26998 | 0.20189 | 0.66387 | 1.0655 | 0.20189 | 0.33628 | 0.13439 | 5.3128 | 1.9979 | 0.33748 | 1 | 5.3336 | 1.7736 | 75.2787
[20 empty] | 20 | 171 | 7.4212 | 176191.302 | 7.7394e+20 | 1.796e-11 | 0.019589 | 2.8393 | 0.26973 | 0.20173 | 0.66382 | 1.0653 | 0.20173 | 0.33603 | 0.1343 | 5.3123 | 1.9974 | 0.33716 | 1 | 5.3323 | 1.9757 | 76.3161
[20 empty] | 21 | 180 | 7.8118 | 185464.5284 | 8.0243e+20 | 7.9047e-12 | 0.0195 | 3.1319 | 0.2695 | 0.20159 | 0.66378 | 1.0651 | 0.20159 | 0.3358 | 0.13421 | 5.3119 | 1.997 | 0.33688 | 1 | 5.3312 | 2.1887 | 77.4068
Piping Inside Diameter, Inches
| Sch / Thickness |  |  | Nominal Pipe Size | 0.375 | 0.5 | 1 | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | OD
1 | 0.375 | 1 | 1 | 0.5 | [6 empty] | 0.622 |  | 0.546 |  |  |  | 0.466 | 0.84 | 1
2 | 0.5 | 2 | 2 | 0.75 | [6 empty] | 0.824 |  | 0.742 |  |  |  | 0.612 | 1.05 | 2
3 | 1 | 3 | 3 | 1 | 0.565 | [5 empty] | 1.049 |  | 0.957 |  |  |  | 0.815 | 1.315 | 3
4 | 10 | 4 | 4 | 1.5 | 1.15 | [5 empty] | 1.61 |  | 1.5 |  |  |  | 1.338 | 1.9 | 4
5 | 20 | 5 | 5 | 2 | 1.625 | [5 empty] | 2.067 |  | 1.939 |  |  |  | 1.687 | 2.375 | 5
6 | 30 | 6 | 6 | 3 | 2.75 | [5 empty] | 3.068 |  | 2.9 |  |  |  | 2.624 | 3.5 | 6
7 | 40 | 7 | 7 | 4 | 3.75 | [5 empty] | 4.026 |  | 3.826 |  | 3.624 |  | 3.438 | 4.5 | 7
8 | 60 | 8 | 8 | 6 | 5.875 | [5 empty] | 6.065 |  | 5.761 |  | 5.501 |  | 5.187 | 6.625 | 8
9 | 80 | 9 | 9 | 8 | 7.875 | 7.625 |  |  | 8.125 | 8.071 | 7.981 | 7.813 | 7.625 | 7.437 | 7.187 | 7.001 | 6.8713 | 8.625 | 9
10 | 100 | 10 | 10 | 10 | 10 | 9.75 |  |  | 10.25 | 10.136 | 10.02 | 9.75 | 9.562 | 9.312 | 9.062 | 8.75 | 8.5 | 10.75 | 10
11 | 120 | 11 | 11 | 12 | 12 | 11.75 |  |  | 12.25 | 12.06 | 11.938 | 11.626 | 11.374 | 11.062 | 10.75 | 10.5 | 10.126 | 12.75 | 11
12 | 140 | 12 | 12 | 14 | 13.25 | 13 |  | 13.5 | 13.376 | 13.25 | 13.124 | 12.812 | 12.5 | 12.124 | 11.812 | 11.5 | 11.188 | 14 | 12
13 | 160 | 13 | 13 | 16 | 15.25 | 15 |  | 15.5 | 15.376 | 15.25 | 15 | 14.688 | 14.312 | 13.938 | 13.562 | 13.124 | 12.812 | 16 | 13
|  |  | 14 | 18 | 17.25 | 17 |  | 17.5 | 17.376 | 17.124 | 16.876 | 16.5 | 16.124 | 15.688 | 15.25 | 14.876 | 14.438 | 18 | 14
|  |  | 15 | 20 | 19.25 | 19 |  | 19.5 | 19.25 | 19 | 18.812 | 18.376 | 17.938 | 17.438 | 17 | 16.5 | 16.062 | 20 | 15
|  |  | 16 | 24 | 23.25 | 23 |  | 23.5 | 23.25 | 22.876 | 22.624 | 22.062 | 21.562 | 20.938 | 20.376 | 19.876 | 19.312 | 24 | 16
|  |  | 17 | 26 | 25.25 | 25 |  | 25.376 | 25 | [8 empty] | 26 | 17
|  |  | 18 | 28 | 27.25 | 27 |  | 27.376 | 27 | 26.75 | [7 empty] | 28 | 18
|  |  | 19 | 30 | 29.25 | 29 |  | 29.376 | 29 | 28.75 | [7 empty] | 30 | 19
|  |  | 20 | 32 | 31.25 | 31 |  | 31.376 | 31 | 30.75 | 30.624 | [6 empty] | 32 | 20
|  |  | 21 | 34 | 33.25 | 33 |  | 33.312 | 33 | 32.75 | 32.624 | [6 empty] | 34 | 21
|  |  | 22 | 36 | 35.25 | 35 |  | 35.376 | 35 | 34.75 | 34.5 | [6 empty] | 36 | 22
|  |  | 23 | 38 | 37.25 | 37 | [11 empty] | 38 | 23
|  |  | 24 | 40 | 39.25 | 39 | [11 empty] | 40 | 24
|  |  | 25 | 42 | 41.25 | 41 | [11 empty] | 42 | 25
|  |  | 26 | 44 | 43.25 | 43 | [11 empty] | 44 | 26
|  |  | 27 | 46 | 45.25 | 45 | [11 empty] | 46 | 27
|  |  | 28 | 48 | 47.25 | 47 | [11 empty] | 48 | 28
|  |  | 29 | 50 | 49.25 | 49 | [11 empty] | 50 | 29
|  |  | 30 | 52 | 51.25 | 51 | [11 empty] | 52 | 30
|  |  | 31 | 54 | 53.25 | 53 | [11 empty] | 54 | 31
|  |  | 32 | 56 | 55.25 | 55 | [11 empty] | 56 | 32
|  |  | 33 | 58 | 57.25 | 57 | [11 empty] | 58 | 33
|  |  | 34 | 60 | 59.25 | 59 | 58 | [10 empty] | 60 | 34
|  |  | 35 | 66 | 65.25 | 65 | 64 | [10 empty] | 66 | 35
|  |  | 36 | 72 | 71.25 | 71 | 70 | [10 empty] | 72 | 36
|  |  | 37 | 78 | 77.25 | 77 | 76 | [10 empty] | 78 | 37
|  |  | 38 | 84 | 83.25 | 83 | 82 | [10 empty] | 84 | 38
|  |  | 39 | 90 | 89.25 | 89 | 88 | [10 empty] | 90 | 39
|  |  | 40 | 96 | 95.25 | 95 | 94 | [10 empty] | 96 | 40
|  |  | 41 | 102 | 101.25 | 101 | 100 | [10 empty] | 102 | 41
|  |  | 42 | 108 | 107.25 | 107 | 106 | [10 empty] | 108 | 42
|  |  | 43 | 114 | 113.25 | 113 | 112 | [10 empty] | 114 | 43
|  |  | 44 | 120 | 119.25 | 119 | 118 | [10 empty] | 120 | 44
h1
P1
P2
Pipe Diameter - ID1
Pipe Length - L1
Pipe Diameter - ID2
Pipe Length - L2
h2

## Metric
PUMP SIZING CALCULATION
CheGuide.com | [8 empty] | Tag No. |  | P-101 |  |  |  |  | Suction Calculations |  |  |  | Outlet Calculations |  |  |  |  | Head Equation (2nd Order Curve Fitting)
Chemical Engineer's Guide | [8 empty] | Description |  | Feed Pump | [13 empty] | -0.094336 | -0.54034 | 91.4003
[9 empty] | Date |  | 06-May-2017 |  |  |  |  | Selected ID |  | 6 |  | Selected ID |  | 6 |  |  | 0.00042079 | 0.010654 | 0.05087
User Input | [8 empty] | By |  | CheGuide |  |  |  |  | Selected Schedule |  | 7 |  | Selected Schedule |  | 7 |  |  | 1 | 0.064124 | #N/A
[16 empty] | Pipe ID Selected |  | 3.068 | inch | Pipe ID Selected |  | 3.068 | inch
[18 empty] | 3.068 | inch |  |  | 3.068 | inch |  | Efficiency Equation (2nd Order Curve Fitting)
[16 empty] | Area |  | 0.0047694 | m2 | Area |  | 0.0047694 | m2 |  | -0.20306 | 5.5932 | 30.2052
Flowrate |  |  | 21.3 | m³/h | [11 empty] | Velocity |  | 1.2405 | m/s | Velocity |  | 1.2405 | m/s |  | 0.0018183 | 0.046039 | 0.21982
Density |  |  | 1350 | kg/m³ | [11 empty] | Re |  | 318308.3719 |  | Re |  | 318308.3719 |  |  | 0.99955 | 0.2771 | #N/A
Viscosity |  |  | 0.41 | cP | [11 empty] | e/D |  | 0.0005867 |  | e/D |  | 0.0005867
Vapor Pressure |  |  | 1.0342 | bar abs | [11 empty] | A |  | 1.1041e+21 |  | A |  | 1.1041e+21 |  |  | System Curve (2nd Order Curve Fitting)
[16 empty] | B |  | 1.3947e-15 |  | B |  | 1.3947e-15 |  |  | 0.0053234 | 0.0062957 | 41.8774
Differential DP |  |  | 5.8838 | bar | [11 empty] | f |  | 0.018738 |  | f |  | 0.018738 |  |  | 3.3597e-06 | 0.00014227 | 0.001255
Differential Head |  |  | 44.4275 | m | [11 empty] | DP1 |  | 0.24977 | bar/100m | DP |  | 0.24977 | bar/100m |  | 1 | 0.0021026 | #N/A
Hydraulic power |  |  | 3.4777 | kw | [11 empty] | Pressure |  | 1.6125 | bar | Pressure |  | 7.4962 | bar
NPSH available |  |  | 4.3665 | m | [20 empty] | Solution of System & Head Curve | [5 empty] | Efficiency | 61.5439 | %
[25 empty] | -0.099659 | -0.54664 | 49.5229
Suction Condition | [7 empty] | Discharge Condition | [7 empty] | Curve Fitting |  |  |  |  | Maximum Flow |  | 40.8824
Pressure |  | P1 | 1.4632 | bar abs |  |  |  | Pressure |  | P2 | 7.0133 | bar abs | [8 empty] | Division |  | 20 |  | Determinant |  | 20.0404 | TRUE | 4.4767 |  |  | X | Y
Static Head |  | h1 | 1.524 | m |  |  |  | Static Head |  | h2 | 1.5 | m |  |  |  | Flow | Head | Efficiency |  |  | Increment |  | 2.0441 |  | Roots |  | -25.2024 | 19.7173 |  |  |  | 19.7173 | 0
Equipment DP |  |  | 0 | bar |  |  |  | Equipment DP |  |  | 0 | bar |  |  | 1 | 0 | 91.44 | 30 | [6 empty] | Selected Flow |  | 19.7173 | GPM | Head | 44.0711 | ft | 19.7173 | 44.0711
Misc DP |  |  | 0 | bar |  |  |  | Misc DP |  |  | 0 | bar |  |  | 2 | 2.2712 | 89.6112 | 42 |  |  |  | Suction Pipe
[15 empty] | 3 | 5.6781 | 85.344 | 55.5 |  |  | Flow | Velocity | Reynold | A | B | f | DP1 | Elb, 90LR | Elb, 45LR | Tees, Thru | Tees, Bran | Ball | Butterfly | Gate | Globe | Check | Plug | Pipe | Sum K | DP | Suct P | Diff P | System Curve | Pump Head | Efficiency %
Piping | [7 empty] | Piping | [6 empty] | 4 | 9.085 | 78.6384 | 64.5 |  |  | m3/h | m/s | [5 empty] | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | [6 empty] | %
Length |  | L1 | 1 | m |  |  |  | Length |  | L2 | 100 | m |  |  | 5 | 11.3562 | 73.152 | 67.5 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6651 | 5.5468 | 41.8834 | 91.4003 | 30.2052
Pipe Diameter |  |  | 3 | inch |  |  |  | Pipe Diameter |  |  | 3 | inch |  |  | 6 | 17.0344 | 54.864 | 66 |  | 2 | 2.0441 | 0.11905 | 30547.4769 | 1.1014e+20 | 26.9433 | 0.024995 | 0.0030686 | 0.29138 | 0.21526 | 0.66788 | 1.0869 | 0.21526 | 0.35768 | 0.14242 | 5.3529 | 2.038 | 0.36422 | 0.50524 | 4.9471 | 0.00047329 | 1.6646 | 5.5507 | 41.9128 | 89.9016 | 40.7898
Sch/ Thick |  |  | 40 |  |  |  |  | Sch/ Thick |  |  | 40 |  |  |  | 7 | 20.4412 | 40.8432 | 60 |  | 3 | 4.0882 | 0.2381 | 61094.9537 | 2.828e+20 | 0.00041112 | 0.022215 | 0.010909 | 0.27828 | 0.20708 | 0.66543 | 1.0739 | 0.20708 | 0.34458 | 0.1375 | 5.3283 | 2.0135 | 0.34785 | 0.50262 | 4.8782 | 0.0018668 | 1.6631 | 5.561 | 41.9904 | 87.6145 | 49.6775
Pipe ID |  | ID1 | 77.9272 | mm |  |  |  | Pipe ID |  | ID2 | 77.9272 | mm |  |  | 8 | 22.7125 | 30.48 | 52.5 |  | 4 | 6.1324 | 0.35716 | 91642.4306 | 4.4188e+20 | 6.2591e-07 | 0.02101 | 0.023214 | 0.27392 | 0.20435 | 0.66461 | 1.0695 | 0.20435 | 0.34022 | 0.13587 | 5.3201 | 2.0053 | 0.3424 | 0.50175 | 4.8553 | 0.0041805 | 1.6607 | 5.5773 | 42.1137 | 84.5391 | 56.8683
[15 empty] | 9 | 22.7125 | 30.48 | 52.5 |  | 5 | 8.1765 | 0.47621 | 122189.9074 | 5.7892e+20 | 6.2732e-09 | 0.020312 | 0.0399 | 0.27174 | 0.20298 | 0.6642 | 1.0673 | 0.20298 | 0.33803 | 0.13505 | 5.3161 | 2.0012 | 0.33967 | 0.50131 | 4.8438 | 0.0074145 | 1.6573 | 5.5996 | 42.2822 | 80.6753 | 62.3622
Roughness |  |  | 0.04572 | mm |  |  |  | Roughness |  |  | 0.04572 | mm |  |  | 10 | 22.7125 | 30.48 | 52.5 |  | 6 | 10.2206 | 0.59526 | 152737.3843 | 6.9579e+20 | 1.7658e-10 | 0.019851 | 0.060927 | 0.27043 | 0.20217 | 0.66395 | 1.066 | 0.20217 | 0.33672 | 0.13456 | 5.3136 | 1.9987 | 0.33803 | 0.50105 | 4.8369 | 0.011569 | 1.6529 | 5.6279 | 42.4956 | 76.0232 | 66.1591
[20 empty] | 7 | 12.2647 | 0.71431 | 183284.8612 | 7.9585e+20 | 9.5506e-12 | 0.01952 | 0.086273 | 0.26955 | 0.20162 | 0.66379 | 1.0651 | 0.20162 | 0.33585 | 0.13423 | 5.312 | 1.9971 | 0.33694 | 0.50087 | 4.8323 | 0.016643 | 1.6476 | 5.6621 | 42.7537 | 70.5828 | 68.2591
Fittings |  |  | No. | K | DP |  |  | Fittings |  |  | No. | K | DP | [6 empty] | 8 | 14.3089 | 0.83336 | 213832.338 | 8.822e+20 | 8.1074e-13 | 0.019271 | 0.11593 | 0.26893 | 0.20123 | 0.66367 | 1.0645 | 0.20123 | 0.33523 | 0.134 | 5.3108 | 1.9959 | 0.33616 | 0.50075 | 4.829 | 0.022638 | 1.6413 | 5.7022 | 43.0563 | 64.354 | 68.6621
Elbows, 90LR |  |  | 1 | 0.2677 | 0.0027808 |  |  | Elbows, 90LR |  |  | 1 | 0.2677 | 0.0027808 | [6 empty] | 9 | 16.353 | 0.95242 | 244379.8149 | 9.5734e+20 | 9.5722e-14 | 0.019075 | 0.14987 | 0.26846 | 0.20094 | 0.66359 | 1.064 | 0.20094 | 0.33476 | 0.13382 | 5.3099 | 1.9951 | 0.33558 | 0.50065 | 4.8265 | 0.029552 | 1.634 | 5.7481 | 43.4035 | 57.3368 | 67.3683
Elbows, 45LR |  |  | 1 | 0.20046 | 0.0020824 |  |  | Elbows, 45LR |  |  | 1 | 0.20046 | 0.0020824 | [6 empty] | 10 | 18.3971 | 1.0715 | 274927.2917 | 1.0233e+21 | 1.454e-14 | 0.018916 | 0.18811 | 0.2681 | 0.20071 | 0.66352 | 1.0637 | 0.20071 | 0.3344 | 0.13369 | 5.3092 | 1.9944 | 0.33512 | 0.50058 | 4.8246 | 0.037387 | 1.6258 | 5.8 | 43.7951 | 49.5313 | 64.3775
Tees, Thru |  |  | 1 | 0.66344 | 0.0068917 |  |  | Tees, Thru |  |  | 1 | 0.66344 | 0.0068917 | [6 empty] | 11 | 20.4412 | 1.1905 | 305474.7686 | 1.0816e+21 | 2.6943e-15 | 0.018786 | 0.23063 | 0.26781 | 0.20053 | 0.66346 | 1.0634 | 0.20053 | 0.33411 | 0.13358 | 5.3087 | 1.9938 | 0.33476 | 0.50052 | 4.8231 | 0.046143 | 1.6166 | 5.8577 | 44.2311 | 40.9375 | 59.6897
Tees, Branch |  |  | 1 | 1.0633 | 0.011045 |  |  | Tees, Branch |  |  | 1 | 1.0633 | 0.011045 | [6 empty] | 12 | 22.4853 | 1.3096 | 336022.2454 | 1.1335e+21 | 5.8637e-16 | 0.018676 | 0.27743 | 0.26757 | 0.20038 | 0.66342 | 1.0631 | 0.20038 | 0.33387 | 0.13349 | 5.3082 | 1.9934 | 0.33446 | 0.50048 | 4.8219 | 0.055818 | 1.6065 | 5.9214 | 44.7115 | 31.5552 | 53.3051
Ball Valves |  |  |  | 0.20046 |  |  |  | Ball Valves |  |  |  | 0.20046 | [7 empty] | 13 | 24.5295 | 1.4286 | 366569.7223 | 1.1801e+21 | 1.4573e-16 | 0.018582 | 0.32851 | 0.26737 | 0.20026 | 0.66338 | 1.0629 | 0.20026 | 0.33367 | 0.13341 | 5.3079 | 1.993 | 0.33421 | 0.50044 | 4.8208 | 0.066414 | 1.5954 | 5.9909 | 45.2363 | 21.3847 | 45.2235
Butterfly Valves |  |  |  | 0.334 |  |  |  | Butterfly Valves |  |  |  | 0.334 | [7 empty] | 14 | 26.5736 | 1.5477 | 397117.1992 | 1.2221e+21 | 4.0491e-17 | 0.018501 | 0.38386 | 0.2672 | 0.20015 | 0.66335 | 1.0628 | 0.20015 | 0.3335 | 0.13335 | 5.3076 | 1.9927 | 0.334 | 0.5004 | 4.8199 | 0.07793 | 1.5833 | 6.0662 | 45.8054 | 10.4258 | 35.4449
Gate Valves |  |  | 1 | 0.13354 | 0.0013872 |  |  | Gate Valves |  |  | 1 | 0.13354 | 0.0013872 | [6 empty] | 15 | 28.6177 | 1.6667 | 427664.676 | 1.2601e+21 | 1.2371e-17 | 0.018431 | 0.44349 | 0.26706 | 0.20006 | 0.66332 | 1.0626 | 0.20006 | 0.33336 | 0.1333 | 5.3073 | 1.9924 | 0.33382 | 0.50037 | 4.8192 | 0.090366 | 1.5703 | 6.1475 | 46.4189 | -1.3215 | 23.9695
Globe Valves |  |  |  | 5.3085 |  |  |  | Globe Valves |  |  |  | 5.3085 | [7 empty] | 16 | 30.6618 | 1.7858 | 458212.1529 | 1.2948e+21 | 4.102e-18 | 0.018368 | 0.50738 | 0.26693 | 0.19998 | 0.6633 | 1.0625 | 0.19998 | 0.33323 | 0.13325 | 5.3071 | 1.9922 | 0.33367 | 0.50035 | 4.8185 | 0.10372 | 1.5563 | 6.2346 | 47.0766 | -13.8571 | 10.7971
Check Valves |  |  | 1 | 1.9936 | 0.020709 |  |  | Check Valves |  |  |  | 1.9936 | [7 empty] | 17 | 32.706 | 1.9048 | 488759.6297 | 1.3265e+21 | 1.4606e-18 | 0.018313 | 0.57555 | 0.26683 | 0.19991 | 0.66328 | 1.0624 | 0.19991 | 0.33312 | 0.13321 | 5.3068 | 1.992 | 0.33353 | 0.50033 | 4.8179 | 0.118 | 1.5413 | 6.3276 | 47.7787 | -27.1811 | -4.0722
Plug Valves |  |  |  | 0.33463 |  |  |  | Plug Valves |  |  |  | 0.33463 | [7 empty] | 18 | 34.7501 | 2.0239 | 519307.1066 | 1.3556e+21 | 5.5369e-19 | 0.018263 | 0.64798 | 0.26673 | 0.19985 | 0.66326 | 1.0623 | 0.19985 | 0.33303 | 0.13317 | 5.3067 | 1.9918 | 0.33341 | 0.50031 | 4.8174 | 0.1332 | 1.5254 | 6.4264 | 48.5251 | -41.2934 | -20.6385
Pipe Entrance |  |  | 1 | 0.5005 | 0.0051991 |  |  | Pipe Exit |  |  | 1 | 1 | 0.010388 | [6 empty] | 19 | 36.7942 | 2.1429 | 549854.5835 | 1.3824e+21 | 2.2187e-19 | 0.018218 | 0.72468 | 0.26664 | 0.1998 | 0.66325 | 1.0622 | 0.1998 | 0.33294 | 0.13314 | 5.3065 | 1.9916 | 0.3333 | 0.50029 | 4.817 | 0.14931 | 1.5085 | 6.5311 | 49.3157 | -56.194 | -38.9016
[5 empty] | 0.050095 | [7 empty] | 0.034575 | [6 empty] | 20 | 38.8383 | 2.262 | 580402.0603 | 1.4072e+21 | 9.341e-20 | 0.018178 | 0.80564 | 0.26657 | 0.19975 | 0.66323 | 1.0621 | 0.19975 | 0.33286 | 0.13311 | 5.3064 | 1.9915 | 0.33321 | 0.50028 | 4.8166 | 0.16635 | 1.4907 | 6.6417 | 50.1506 | -71.883 | -58.8617
Velocity |  |  | 1.2405 | m/s |  |  |  | Velocity |  |  | 1.2405 | m/s | [7 empty] | 21 | 40.8824 | 2.381 | 610949.5372 | 1.4302e+21 | 4.1112e-20 | 0.018141 | 0.89087 | 0.2665 | 0.19971 | 0.66322 | 1.0621 | 0.19971 | 0.3328 | 0.13309 | 5.3062 | 1.9914 | 0.33312 | 0.50026 | 4.8162 | 0.18431 | 1.4719 | 6.7581 | 51.0298 | -88.3604 | -80.5188
Reynold's No. |  |  | 318308.3719 |  |  |  |  | Reynold's No. |  |  | 318308.3719
Pipe DP |  |  | 0.24977 | bar/100m |  |  |  | Pipe DP |  |  | 0.24977 | bar/100m | [9 empty] | Discharge Conditions
Suction Pressure |  |  | 1.6125 | bar |  |  |  | Discharge Pressure |  |  | 7.4962 | bar | [8 empty] | Flow | Velocity | Reynold | A | B | f | DP1 | Elb, 90LR | Elb, 45LR | Tees, Thru | Tees, Bran | Ball | Butterfly | Gate | Globe | Check | Plug | Pipe | Sum K | DP | Disch P
[21 empty] | GPM | m/s | [5 empty] | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1
[20 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 7.2119
| Pump Manufacturer's Curve | [6 empty] | Maximum Flow |  |  | 40.8824 | m³/h | [7 empty] | 2 | 2.0441 | 0.11905 | 30547.4769 | 1.1014e+20 | 26.9433 | 0.024995 | 0.0030686 | 0.29138 | 0.21526 | 0.66788 | 1.0869 | 0.21526 | 0.35768 | 0.14242 | 5.3529 | 2.038 | 0.36422 | 1 | 3.4039 | 0.00032565 | 7.2153
[8 empty] | Flow value till which System and Head Curve | [11 empty] | 3 | 4.0882 | 0.2381 | 61094.9537 | 2.828e+20 | 0.00041112 | 0.022215 | 0.010909 | 0.27828 | 0.20708 | 0.66543 | 1.0739 | 0.20708 | 0.34458 | 0.1375 | 5.3283 | 2.0135 | 0.34785 | 1 | 3.3621 | 0.0012866 | 7.2241
| Flow | Head | Efficiency |  |  |  |  | are calculated | [11 empty] | 4 | 6.1324 | 0.35716 | 91642.4306 | 4.4188e+20 | 6.2591e-07 | 0.02101 | 0.023214 | 0.27392 | 0.20435 | 0.66461 | 1.0695 | 0.20435 | 0.34022 | 0.13587 | 5.3201 | 2.0053 | 0.3424 | 1 | 3.3482 | 0.0028829 | 7.238
| m³/h | m | % | [16 empty] | 5 | 8.1765 | 0.47621 | 122189.9074 | 5.7892e+20 | 6.2732e-09 | 0.020312 | 0.0399 | 0.27174 | 0.20298 | 0.6642 | 1.0673 | 0.20298 | 0.33803 | 0.13505 | 5.3161 | 2.0012 | 0.33967 | 1 | 3.3413 | 0.0051146 | 7.2569
| 0 | 91.44 | 30 |  |  |  |  | Operating Conditions | [11 empty] | 6 | 10.2206 | 0.59526 | 152737.3843 | 6.9579e+20 | 1.7658e-10 | 0.019851 | 0.060927 | 0.27043 | 0.20217 | 0.66395 | 1.066 | 0.20217 | 0.33672 | 0.13456 | 5.3136 | 1.9987 | 0.33803 | 1 | 3.3371 | 0.0079815 | 7.2808
| 2.2712 | 89.6112 | 42 |  |  |  |  | Flowrate |  |  | 19.7173 | m³/h | [7 empty] | 7 | 12.2647 | 0.71431 | 183284.8612 | 7.9585e+20 | 9.5506e-12 | 0.01952 | 0.086273 | 0.26955 | 0.20162 | 0.66379 | 1.0651 | 0.20162 | 0.33585 | 0.13423 | 5.312 | 1.9971 | 0.33694 | 1 | 3.3343 | 0.011484 | 7.3097
| 5.6781 | 85.344 | 55.5 |  |  |  |  | Head |  |  | 44.0711 | m | [7 empty] | 8 | 14.3089 | 0.83336 | 213832.338 | 8.822e+20 | 8.1074e-13 | 0.019271 | 0.11593 | 0.26893 | 0.20123 | 0.66367 | 1.0645 | 0.20123 | 0.33523 | 0.134 | 5.3108 | 1.9959 | 0.33616 | 1 | 3.3323 | 0.015621 | 7.3434
| 9.085 | 78.6384 | 64.5 |  |  |  |  | Efficiency |  |  | 61.5439 | % | [7 empty] | 9 | 16.353 | 0.95242 | 244379.8149 | 9.5734e+20 | 9.5722e-14 | 0.019075 | 0.14987 | 0.26846 | 0.20094 | 0.66359 | 1.064 | 0.20094 | 0.33476 | 0.13382 | 5.3099 | 1.9951 | 0.33558 | 1 | 3.3308 | 0.020394 | 7.3822
| 11.3562 | 73.152 | 67.5 |  |  |  |  | Hydraulic Power |  |  | 3.1967 | kW | [7 empty] | 10 | 18.3971 | 1.0715 | 274927.2917 | 1.0233e+21 | 1.454e-14 | 0.018916 | 0.18811 | 0.2681 | 0.20071 | 0.66352 | 1.0637 | 0.20071 | 0.3344 | 0.13369 | 5.3092 | 1.9944 | 0.33512 | 1 | 3.3297 | 0.025803 | 7.4258
| 17.0344 | 54.864 | 66 |  |  |  |  | Rated Power |  |  | 5.1942 | kW | [7 empty] | 11 | 20.4412 | 1.1905 | 305474.7686 | 1.0816e+21 | 2.6943e-15 | 0.018786 | 0.23063 | 0.26781 | 0.20053 | 0.66346 | 1.0634 | 0.20053 | 0.33411 | 0.13358 | 5.3087 | 1.9938 | 0.33476 | 1 | 3.3288 | 0.031846 | 7.4744
| 20.4412 | 40.8432 | 60 | [16 empty] | 12 | 22.4853 | 1.3096 | 336022.2454 | 1.1335e+21 | 5.8637e-16 | 0.018676 | 0.27743 | 0.26757 | 0.20038 | 0.66342 | 1.0631 | 0.20038 | 0.33387 | 0.13349 | 5.3082 | 1.9934 | 0.33446 | 1 | 3.328 | 0.038525 | 7.5279
| 22.7125 | 30.48 | 52.5 | [16 empty] | 13 | 24.5295 | 1.4286 | 366569.7223 | 1.1801e+21 | 1.4573e-16 | 0.018582 | 0.32851 | 0.26737 | 0.20026 | 0.66338 | 1.0629 | 0.20026 | 0.33367 | 0.13341 | 5.3079 | 1.993 | 0.33421 | 1 | 3.3274 | 0.045839 | 7.5863
[20 empty] | 14 | 26.5736 | 1.5477 | 397117.1992 | 1.2221e+21 | 4.0491e-17 | 0.018501 | 0.38386 | 0.2672 | 0.20015 | 0.66335 | 1.0628 | 0.20015 | 0.3335 | 0.13335 | 5.3076 | 1.9927 | 0.334 | 1 | 3.3268 | 0.053789 | 7.6496
[20 empty] | 15 | 28.6177 | 1.6667 | 427664.676 | 1.2601e+21 | 1.2371e-17 | 0.018431 | 0.44349 | 0.26706 | 0.20006 | 0.66332 | 1.0626 | 0.20006 | 0.33336 | 0.1333 | 5.3073 | 1.9924 | 0.33382 | 1 | 3.3264 | 0.062374 | 7.7178
[20 empty] | 16 | 30.6618 | 1.7858 | 458212.1529 | 1.2948e+21 | 4.102e-18 | 0.018368 | 0.50738 | 0.26693 | 0.19998 | 0.6633 | 1.0625 | 0.19998 | 0.33323 | 0.13325 | 5.3071 | 1.9922 | 0.33367 | 1 | 3.326 | 0.071594 | 7.7909
[20 empty] | 17 | 32.706 | 1.9048 | 488759.6297 | 1.3265e+21 | 1.4606e-18 | 0.018313 | 0.57555 | 0.26683 | 0.19991 | 0.66328 | 1.0624 | 0.19991 | 0.33312 | 0.13321 | 5.3068 | 1.992 | 0.33353 | 1 | 3.3256 | 0.08145 | 7.8689
[20 empty] | 18 | 34.7501 | 2.0239 | 519307.1066 | 1.3556e+21 | 5.5369e-19 | 0.018263 | 0.64798 | 0.26673 | 0.19985 | 0.66326 | 1.0623 | 0.19985 | 0.33303 | 0.13317 | 5.3067 | 1.9918 | 0.33341 | 1 | 3.3253 | 0.091941 | 7.9518
[20 empty] | 19 | 36.7942 | 2.1429 | 549854.5835 | 1.3824e+21 | 2.2187e-19 | 0.018218 | 0.72468 | 0.26664 | 0.1998 | 0.66325 | 1.0622 | 0.1998 | 0.33294 | 0.13314 | 5.3065 | 1.9916 | 0.3333 | 1 | 3.325 | 0.10307 | 8.0396
[20 empty] | 20 | 38.8383 | 2.262 | 580402.0603 | 1.4072e+21 | 9.341e-20 | 0.018178 | 0.80564 | 0.26657 | 0.19975 | 0.66323 | 1.0621 | 0.19975 | 0.33286 | 0.13311 | 5.3064 | 1.9915 | 0.33321 | 1 | 3.3248 | 0.11483 | 8.1324
[20 empty] | 21 | 40.8824 | 2.381 | 610949.5372 | 1.4302e+21 | 4.1112e-20 | 0.018141 | 0.89087 | 0.2665 | 0.19971 | 0.66322 | 1.0621 | 0.19971 | 0.3328 | 0.13309 | 5.3062 | 1.9914 | 0.33312 | 1 | 3.3246 | 0.12723 | 8.23
Piping Inside Diameter, Inches
| Sch / Thickness |  |  | Nominal Pipe Size | 0.375 | 0.5 | 1 | 10 | 20 | 30 | 40 | 60 | 80 | 100 | 120 | 140 | 160 | OD
1 | 0.375 | 1 | 1 | 0.5 | [6 empty] | 0.622 |  | 0.546 |  |  |  | 0.466 | 0.84 | 1
2 | 0.5 | 2 | 2 | 0.75 | [6 empty] | 0.824 |  | 0.742 |  |  |  | 0.612 | 1.05 | 2
3 | 1 | 3 | 3 | 1 | 0.565 | [5 empty] | 1.049 |  | 0.957 |  |  |  | 0.815 | 1.315 | 3
4 | 10 | 4 | 4 | 1.5 | 1.15 | [5 empty] | 1.61 |  | 1.5 |  |  |  | 1.338 | 1.9 | 4
5 | 20 | 5 | 5 | 2 | 1.625 | [5 empty] | 2.067 |  | 1.939 |  |  |  | 1.687 | 2.375 | 5
6 | 30 | 6 | 6 | 3 | 2.75 | [5 empty] | 3.068 |  | 2.9 |  |  |  | 2.624 | 3.5 | 6
7 | 40 | 7 | 7 | 4 | 3.75 | [5 empty] | 4.026 |  | 3.826 |  | 3.624 |  | 3.438 | 4.5 | 7
8 | 60 | 8 | 8 | 6 | 5.875 | [5 empty] | 6.065 |  | 5.761 |  | 5.501 |  | 5.187 | 6.625 | 8
9 | 80 | 9 | 9 | 8 | 7.875 | 7.625 |  |  | 8.125 | 8.071 | 7.981 | 7.813 | 7.625 | 7.437 | 7.187 | 7.001 | 6.8713 | 8.625 | 9
10 | 100 | 10 | 10 | 10 | 10 | 9.75 |  |  | 10.25 | 10.136 | 10.02 | 9.75 | 9.562 | 9.312 | 9.062 | 8.75 | 8.5 | 10.75 | 10
11 | 120 | 11 | 11 | 12 | 12 | 11.75 |  |  | 12.25 | 12.06 | 11.938 | 11.626 | 11.374 | 11.062 | 10.75 | 10.5 | 10.126 | 12.75 | 11
12 | 140 | 12 | 12 | 14 | 13.25 | 13 |  | 13.5 | 13.376 | 13.25 | 13.124 | 12.812 | 12.5 | 12.124 | 11.812 | 11.5 | 11.188 | 14 | 12
13 | 160 | 13 | 13 | 16 | 15.25 | 15 |  | 15.5 | 15.376 | 15.25 | 15 | 14.688 | 14.312 | 13.938 | 13.562 | 13.124 | 12.812 | 16 | 13
|  |  | 14 | 18 | 17.25 | 17 |  | 17.5 | 17.376 | 17.124 | 16.876 | 16.5 | 16.124 | 15.688 | 15.25 | 14.876 | 14.438 | 18 | 14
|  |  | 15 | 20 | 19.25 | 19 |  | 19.5 | 19.25 | 19 | 18.812 | 18.376 | 17.938 | 17.438 | 17 | 16.5 | 16.062 | 20 | 15
|  |  | 16 | 24 | 23.25 | 23 |  | 23.5 | 23.25 | 22.876 | 22.624 | 22.062 | 21.562 | 20.938 | 20.376 | 19.876 | 19.312 | 24 | 16
|  |  | 17 | 26 | 25.25 | 25 |  | 25.376 | 25 | [8 empty] | 26 | 17
|  |  | 18 | 28 | 27.25 | 27 |  | 27.376 | 27 | 26.75 | [7 empty] | 28 | 18
|  |  | 19 | 30 | 29.25 | 29 |  | 29.376 | 29 | 28.75 | [7 empty] | 30 | 19
|  |  | 20 | 32 | 31.25 | 31 |  | 31.376 | 31 | 30.75 | 30.624 | [6 empty] | 32 | 20
|  |  | 21 | 34 | 33.25 | 33 |  | 33.312 | 33 | 32.75 | 32.624 | [6 empty] | 34 | 21
|  |  | 22 | 36 | 35.25 | 35 |  | 35.376 | 35 | 34.75 | 34.5 | [6 empty] | 36 | 22
|  |  | 23 | 38 | 37.25 | 37 | [11 empty] | 38 | 23
|  |  | 24 | 40 | 39.25 | 39 | [11 empty] | 40 | 24
|  |  | 25 | 42 | 41.25 | 41 | [11 empty] | 42 | 25
|  |  | 26 | 44 | 43.25 | 43 | [11 empty] | 44 | 26
|  |  | 27 | 46 | 45.25 | 45 | [11 empty] | 46 | 27
|  |  | 28 | 48 | 47.25 | 47 | [11 empty] | 48 | 28
|  |  | 29 | 50 | 49.25 | 49 | [11 empty] | 50 | 29
|  |  | 30 | 52 | 51.25 | 51 | [11 empty] | 52 | 30
|  |  | 31 | 54 | 53.25 | 53 | [11 empty] | 54 | 31
|  |  | 32 | 56 | 55.25 | 55 | [11 empty] | 56 | 32
|  |  | 33 | 58 | 57.25 | 57 | [11 empty] | 58 | 33
|  |  | 34 | 60 | 59.25 | 59 | 58 | [10 empty] | 60 | 34
|  |  | 35 | 66 | 65.25 | 65 | 64 | [10 empty] | 66 | 35
|  |  | 36 | 72 | 71.25 | 71 | 70 | [10 empty] | 72 | 36
|  |  | 37 | 78 | 77.25 | 77 | 76 | [10 empty] | 78 | 37
|  |  | 38 | 84 | 83.25 | 83 | 82 | [10 empty] | 84 | 38
|  |  | 39 | 90 | 89.25 | 89 | 88 | [10 empty] | 90 | 39
|  |  | 40 | 96 | 95.25 | 95 | 94 | [10 empty] | 96 | 40
|  |  | 41 | 102 | 101.25 | 101 | 100 | [10 empty] | 102 | 41
|  |  | 42 | 108 | 107.25 | 107 | 106 | [10 empty] | 108 | 42
|  |  | 43 | 114 | 113.25 | 113 | 112 | [10 empty] | 114 | 43
|  |  | 44 | 120 | 119.25 | 119 | 118 | [10 empty] | 120 | 44
h1
P1
P2
Pipe Diameter - ID1
Pipe Length - L1
Pipe Diameter - ID2
Pipe Length - L2
h2